SECTION 223436.23 – HIGH EFFICIENCY GAS DOMESTIC WATER HEATERS

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract apply to this Section, including General and Supplementary Conditions and Division 01 Specification Sections.

      - SUMMARY

        - This Section includes packaged, factory-fabricated and -assembled, propane-fired, high efficiency condensing domestic water heaters, trim and accessories for generating hot potable water.

      - SUBMITTALS

        - Product Data: Include performance data, operating characteristics, furnished specialties and accessories.

          - Prior to flue vent installation, engineered calculations and drawings must be submitted to Architect/Engineer to thoroughly demonstrate that size and configuration conform to recommended size, length and footprint for each submitted water heater.

        - Pressure Drop Curve: Submit pressure drop curve for flows ranging from 0 GPM to maximum value of water heater.

        - Shop Drawings: For water heaters, water heater trim and accessories, include:

          - Plans, elevations, sections, details and attachments to other work

          - Wiring Diagrams for power, signal and control wiring

        - Source Quality Control Test Reports: Reports shall be included in submittals.

        - Field Quality Control Test Reports: Reports shall be included in submittals.

        - Operation and Maintenance Data: Data to be included in water heater emergency, operation and maintenance manuals.

        - Warranty: Standard warranty specified in this Section.

        - Other Informational Submittals.

          - ASME Stamp Certification and Report: Submit "A," "S," or "PP" stamp certificate of authorization, as required by authorities having jurisdiction, and document hydrostatic testing of piping external to water heater.

      - QUALITY ASSURANCE

        - Electrical Components, Devices and Accessories: Condensing water heaters must be listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

        - ASME Compliance: Condensing water heaters must be constructed in accordance with ASME Water heater and Pressure Vessel Code, Section IV (HLW) Potable Water Heaters.

        - ASHRAE/IESNA 90.1 Compliance: Condensing water heaters shall have minimum efficiency according to "Gas and Oil Fired water heaters - Minimum Efficiency Requirements," when tested in accordance with Section G.1 “Method of Test for Measuring Thermal Efficiency” and G.2 “Method of Test for Measuring Standby Loss” of ANSI Z21.10.3

        - UL Compliance. Condensing water heaters must be tested for compliance with UL 795, "Commercial-Industrial Gas Heating Equipment." Condensing water heaters shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

      - COORDINATION

        - Coordinate size and location of concrete bases. Cast anchor-bolt inserts into bases. Concrete, reinforcement and formwork requirements are specified in Division 03.

      - WARRANTY

        - Standard Warranty: Water heaters shall include manufacturer's standard form in which manufacturer agrees to repair or replace components of water heaters that fail in materials or workmanship within specified warranty period.

          - Warranty Period for Fire-Tube Condensing Water heaters:

- The pressure vessel shall carry a 10-year from shipment, non-prorated, limited warranty against any failure due to waterside corrosion, mechanical defects, or workmanship. The heat exchanger shall carry a 10-year from shipment, prorated, limited warranty against any failure due to condensate corrosion, thermal stress, mechanical defects, or workmanship.

- Manufacturer labeled control panels are conditionally warranted against failure for two (2) years from shipment.

- All other components, with the exception of the igniter and flame detector, are conditionally guaranteed against any failure for 18 months from shipment.

- PRODUCTS

      - MANUFACTURERS

        - Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

        - Basis-of-Design Product: Subject to compliance with requirements, provide AERCO INNOVATION,  Model INN600___ ; INN800___ ; INN1060___ ; INN1350___ ; or a comparable product by one of the following:

          - AERCO International, Inc.

          - _____________________

          - _____________________

      - CONSTRUCTION

        - General: The water heating plant shall have a total recovery of _______ GPH, (_____ GPM) at a _____oF temperature rise.  Each water heater shall be UL Listed; ASME Section IV (HLW) coded and stamped and shall incorporate an ___ FM or ___ a double block and bleed style -formerly IRI. Gas train.    Each unit shall operate with a minimum ASHRAE 118.1 efficiency of 96% at full fire. System shall consist of a quantity of      Water Heaters Model:

- ___INN600 each with an input of 600 MBH, output of 578 MBH, 696 GPH, (11.6 GPM) at 40-140 oF when fired with propane, turndown ratio up to 14:1.

- ___INN800 each with an input of 800 MBH, output of 771 MBH, 924 GPH, (15.4 GPM) at 40-140 oF when fired with propane, turndown ratio up to 18:1.

- ___INN1060 each with an input of 1060 MBH, output of 1022 MBH, 1224 GPH, (20.4 GPM) at 40-140 oF when fired with propane, turndown ratio up to 24:1.

- ___INN1350 each with an input of 1350 MBH, output of 1300 MBH, 1560 GPH, (26 GPM) at 40-140 oF when fired with propane, turndown ratio up to 30:1.

        - Description: Water heater shall be propane fired, fully condensing, fire-tube design. Power burner shall have full modulation. The minimum firing rate of 50,000 BTU/HR input shall be possible. Water heaters that have an input greater than 50,000 BTU/Hr at minimum fire will not be considered equal. The water heater shall have the capability of discharging into a positive pressure vent. Water heater thermal efficiency shall increase with decreasing load (output), while maintaining setpoint. Water heater shall have an operational setpoint capability of 50 ºF to 190 ºF and shall maintain the outlet temperature within an accuracy of +/- 4 oF during load changes of up to 50% rated capacity. Heater shall operate quietly, less than 55 dba.  Water heater shall be factory-fabricated, factory-assembled and factory-tested, fire-tube condensing water heater with heat exchanger sealed pressure-tight, built on a steel base, including a sealed insulated sheet metal enclosure that acts as combustion-air intake plenum, flue-gas vent, water supply, return and condensate drain connections, and controls. Each water heater shall have an ASME approved temperature/pressure relief valve with a setting of 150 psig and 210 oF.

        - Heat Exchanger: The heat exchanger shall be constructed with 316L stainless steel helical fire tubes, combustion chamber and dished tubesheet, with a two-pass combustion gas flow design. The heat exchanger shall be electroless nickel plated.  The fire tubes shall be 3/4” OD, with no less than 0.035” wall thickness. The upper and lower stainless steel tubesheet shall be no less than 0.625” thick. The heat exchanger shall be welded and brazed construction. The heat exchanger shall be ASME Sect IV (HLW) stamped for a working pressure not less than 160 psig.

        - Shell Assembly Pressure Vessel: The shell assembly pressure vessel shall have a maximum water volume of 26 gallons. The water heater water pressure drop shall not exceed 2 psig at 30 gpm. The water heater water connections shall be 2-inch NPT male connections. The shell assembly pressure vessel shall be constructed of 304 stainless steel of 0.25-inch wall thickness. The shell assembly pressure vessel shall be electroless nickel plated.  Inspection openings in the pressure vessel shall be in accordance with ASME Section IV pressure vessel code.  The shell assembly pressure vessel shall be ASME Sect IV (HLW) stamped for a working pressure not less than 160 psig.

        - Modulating Air/Fuel Valve and Burner: The water heater burner shall be capable of up to __14-to-1(INN600), __18-to-1(INN800), __24-to-1(INN1060), __30-to-1(INN1350) turndown ratio of the firing rate without loss of combustion efficiency or staging of gas valves. The burner shall be metal-fiber mesh covering a stainless steel body with spark ignition and flame rectification. All burner material exposed to the combustion zone shall be of stainless steel construction. There shall be no moving parts within the burner itself. A modulating air/fuel valve shall meter the air and fuel input. The modulating motor must be linked to both the gas valve body and air valve body with a single linkage. The linkage shall not require any field adjustment. A variable frequency drive (VFD), controlled cast aluminum pre-mix blower shall be used to ensure the optimum mixing of air and fuel between the air/fuel valve and the burner.

        - The exhaust manifold shall be of corrosion resistant cast aluminum with a 6-inch diameter flue connection. The exhaust manifold shall have a collecting reservoir and a gravity drain for the elimination of condensation.

        - Blower. The water heater shall include a variable-speed, DC centrifugal fan to operate during the burner firing sequence and pre-purge the combustion chamber.

          - Motors: Blower motors shall comply with requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

- Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require a motor to operate in the service factor range above 1.0.

        - Ignition: Ignition shall be via spark ignition with 100 percent main-valve shutoff and electronic flame supervision.

      - CONTROLS

        - Refer to Division 23, Section “Instrumentation and Control of HVAC.”

        - The water heater control system shall be segregated into three components: “C-More” Control Panel, Power Box and Input/Output Connection Box. The entire system shall be Underwriters Laboratories recognized.

        - The control panel shall consist of six individual circuit boards using state-of-the-art surface-mount technology in a single enclosure. These circuit boards shall include:

          - A display board incorporating LED display to indicate temperature and a vacuum fluorescent display module for all message enunciation

          - A CPU board housing all control functions

          - An electric low-water cutoff board with test and manual reset functions

          - A power supply board

          - An ignition /stepper board incorporating flame safeguard control

          - A connector board

- Each board shall be individually field replaceable.

        - The combustion safeguard/flame monitoring system shall use spark ignition and a rectification-type flame sensor.

        - The control panel hardware shall support both RS-232 and RS-485 remote communications.

        - The controls shall annunciate water heater and sensor status and include extensive self-diagnostic capabilities that incorporate a minimum of eight separate status messages and 34 separate fault messages.

        - The control panel shall incorporate three self-governing features designed to enhance operation in modes where it receives an external control signal by eliminating nuisance faults due to over-temperature, improper external signal or loss of external signal. These features include:

          - Setpoint High Limit: Setpoint high limit allows for a selectable maximum water heater outlet temperature and acts as temperature limiting governor. Setpoint limit is based on a PID function that automatically limits firing rate to maintain outlet temperature within a 0 to 10 degree selectable band from the desired maximum water heater outlet temperature.

          - Setpoint Low Limit: Setpoint low limit allows for a selectable minimum operating temperature.

          - Failsafe Mode: Failsafe mode allows the water heater to switch its mode to operate from an internal setpoint if its external control signal is lost, rather than shut off. This is a selectable mode, enabling the control can to shut off the unit upon loss of external signal, if so desired.

        - The water heater control system shall incorporate the following additional features for enhanced external system interface:

          - System start temperature feature

          - Pump delay timer

          - Auxiliary start delay timer

          - Auxiliary temperature sensor

          - Analog output feature to enable simple monitoring of temperature setpoint, outlet temperature or fire rate

          - Remote interlock circuit

          - Delayed interlock circuit

          - Fault relay for remote fault alarm

        - Water Heater Management: the water heater control system shall incorporate onboard multi-unit sequencing logic that would allow lead-lag functionality & sequencing between multiple water heaters operating in parallel and must have the following capabilities:

          - Efficiently sequence 2 up to 8 units on the same system to meet the load requirement.

          - Individual unit feed-forward logic will still be enabled for accurate temperature control equal to individual unit’s specification.

          - Operate one motorized valve per unit as an element of the load sequencing, Valves shall close with decreased load as heaters turn off, minimum of one (quantity must be selectable) must always stay open for recirculation.

          - Automatically rotate lead/lag amongst the units on the chain and monitor run hours per unit and balance load in an effort to equalize unit run hours.

          - Automatic bump-less transfer of master function to next unit on the chain in case of designated master unit failure; master/slave status should be shown on the individual unit displays.

          - Units will default to individual control upon failure of the communications chain.

          - Night temperature setback.

          - Designated master control, used to display and adjust key system parameters.

        - ___Each water heater shall be supplied with a factory packaged and pre-wired motorized ball valve.  This valve shall be controlled by the water heater control system as an element of the onboard water heater management.

        - Each water heater shall include an electric, single-seated combination safety shutoff valve/regulator with proof of closure switch in its gas train. Each water heater shall incorporate dual over-temperature protection with manual reset, in accordance with ASME Section IV and CSD-1.

      - ELECTRICAL POWER

        - Controllers, Electrical Devices and Wiring: Electrical devices and connections are specified in Division 26 sections.

        - Single-Point Field Power Connection: Factory-installed and factory-wired switches, motor controllers, transformers and other electrical devices shall provide a single-point field power connection to the water heater.

        - Electrical Characteristics:

          - Voltage: 	120 V

          - Phase: 	Single

          - Frequency: 	60 Hz

          - Full-Load Current 	11 Amps

      - VENTING

        - The exhaust vent must be UL Listed for use with Category II, III and IV appliances and compatible with positive pressure, condensing flue gas service. UL- listed vents of PVC, CPVC, PP, or Al 29-4C stainless steel must be used with water heaters.

        - The minimum exhaust vent duct size for each water heater is six-inch diameter.

        - Combustion-Air Intake: Water heaters shall be capable of drawing combustion air from the outdoors via a metal or PVC duct connected between the water heater and the outdoors.

        - The minimum sealed combustion air duct size for each water heater is six-inch diameter.

        - Common Vent and Common Combustion Air must be an available option for water heater installation. Consult manufacturer for common vent and combustion air sizing.

        - Follow guidelines specified in manufacturer’s venting guide.

      - SOURCE QUALITY CONTROL

        - Burner and Hydrostatic Test: Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions and carbon monoxide in flue gas, and to achieve combustion efficiency. Perform hydrostatic testing.

        - Test and inspect factory-assembled water heaters, before shipping, according to ASME Boiler and Pressure Vessel Code.

          - If water heaters are not factory assembled and fire-tested, the local vendor is responsible for all field assembly and testing.

        - Allow Owner access to source quality-control testing of water heaters. Notify Architect fourteen days in advance of testing.

- EXECUTION

      - EXAMINATION

        - Before water heater installation, examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations. Examine piping and electrical connections to verify actual locations, sizes and other conditions affecting water heater performance, maintenance and operations.

          - Final water heater locations indicated on Drawings are approximate. Determine exact locations before roughing-in for piping and electrical connections.

        - Examine mechanical spaces for suitable conditions where water heaters will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - WATER HEATER INSTALLATION

        - Install water heaters level on concrete bases. Concrete base is specified in Division 23 Section "Common Work Results for HVAC," and concrete materials and installation requirements are specified in Division 03.

        - Install gas-fired water heaters in accordance with

          - Local, stats provincial, and national codes, laws, regulations, and ordinances.

          - National Fuel Gas Code, ANSI Z223.1/NFPA 54 – latest edition.

          - National Electrical Code, ANSI/NFPA 70 - latest edition.

          - Canada only: CAN/CGA B149 Installation Code and CSA C22.1 CEC Part 1.

          - Manufacturer’s installation instructions, including required service clearances and venting guidelines.

        - Assemble and install water heater trim.

        - Install electrical devices furnished with water heater but not specified to be factory mounted.

        - Install control wiring to field-mounted electrical devices.

      - CONNECTIONS

        - Piping installation requirements are specified in other Division 23 sections. Drawings indicate general arrangement of piping, fittings and specialties.

        - Install piping adjacent to water heater to permit service and maintenance.

        - Install piping from equipment drain connection to nearest floor drain. Piping shall be at least full size of connection. Provide an isolation valve if required.

        - Connect gas piping to water heater gas-train inlet with unions. Piping shall be at least full size of gas train connection. Provide a reducer if required.

        - Connect hot-water piping to supply and return water heater tappings with shutoff valve and union or flange at each connection.

        - Install piping from safety relief valves to nearest floor drain.

        - Water heater Venting

          - Install flue venting kit and combustion-air intake.

          - Connect venting full size to water heater connections. [Comply with requirements in Division 23 Section "Breechings, Chimneys and Stacks."]

        - Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

        - Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

      - FIELD QUALITY CONTROL

        - Perform tests and inspections and prepare test reports.

          - Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies and equipment installations, including connections, and to assist in testing.

        - Tests and Inspections

          - Installation and Startup Test: Perform installation and startup checks according to manufacturer's written instructions.

          - Leak Test: Perform hydrostatic test. Repair leaks and retest until no leaks exist.

          - Operational Test: Start units to confirm proper motor rotation and unit operation. Adjust air-fuel ratio and combustion.

          - Controls and Safeties: Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

- a.	Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level and water temperature.

- b.	Set field-adjustable switches and circuit-breaker trip ranges as indicated.

        - Remove and replace malfunctioning units and retest as specified above.

        - Occupancy Adjustments: When requested within 2 months of date of Substantial Completion, provide on-site assistance adjusting system to suit actual occupied conditions. Provide up to two visits to Project during other than normal occupancy hours for this purpose.

        - Performance Tests

- The water heater manufacturer is expected to provide partial load thermal efficiency curves. These thermal efficiency curves must include at least three separate curves at various BTU input levels. If these curves are not available, it is the responsibility of the water heater manufacturer to complete the following performance tests:

          - Engage a factory-authorized service representative to inspect component assemblies and equipment installations, including connections, and to conduct performance testing.

          - Water heaters shall comply with performance requirements indicated, as determined by field performance tests. Adjust, modify, or replace equipment to comply.

          - Perform field performance tests to determine capacity and efficiency of water heaters.

          - Repeat tests until results comply with requirements indicated.

          - Provide analysis equipment required to determine performance.

          - Provide temporary equipment and system modifications necessary to dissipate the heat produced during tests if building systems are not adequate.

          - Notify Architect in advance of test dates.

          - Document test results in a report and submit to Architect.

END OF SECTION 223436.23